## Slide 1: DER Technical Forum
03 November 2020
Join Microsoft Teams Meeting
+44 20 3855 5885 United Kingdom, London (Toll)
Conference ID: 462 309 959#

## Slide 2: Agenda
Time | Focus | Leader
09:00 | Welcome, Introductions and Acceptance of Agenda. | CM
09:02 | Acceptance of minutes of previous meeting (01 September 2020) | CM
09:05 | Update etc on TTR for those not attending the TTR session later in the day | CM/MD
09:10 | New issues raised (none to date) | 
09:15 | Remaining Open Issues: 101 – load rejection simulations for Type C and D | MK
09:20 | Housekeeping Members’ issues Update on drafting etc | All MK/SRC
09:50 | Storage Modifications Update | CM/MK/SRC
10:20 | G100 – update | AH/MK
10:30 | Brexit and EU developments | CM/MK
10:40 | AOB | 
10:45 | Next meeting | 

## Slide 3: Welcome, Housekeeping and Introductions

## Slide 4: Minutes of previous meeting and actions
Matters arising not on the agenda:
  None?

## Slide 5: Type Test Register

## Slide 6: New Issues

## Slide 7: Unresolved Previous Issue
No | Issue | Assumed Status
101 | The issue is the LFSM-O load rejection test, and the scenario given in Appendix C7.5. For a project I have setup a test network for a Type C solar PV site, rated at 15MW and connected at 33kV which has generated some queries. Specifically: It is not clear what the ultimate aim of the test is? ie is it just to show the speed at which the inverters can de-load in the case of an over-frequency condition (ie like the equivalent Type B LFSM-O simple ramp test), or is it to show the system can actually form an island - which doesn’t make sense as the inverters do not have grid forming capability. The value ‘X’ seems to be arbitrary, and the standard wording implies that we just adjust this value until we get the required 52Hz deviation and add the generator rating to this value? Is this above assumption correct or is the value X supposed to be the Design Minimum Operating Level (DMOL)? Whilst practically a solar PV plants minimum, operating level can be very low at say 5% or less, but the inverters would not be able to handle a load rejection of 95%, and most DNO connection agreements, don’t give specific values in the way Grid connection offers do. What is the guidance for selecting the rating of the dummy generator ‘G2’, I have found that setting the value to the same rating as the site, seems to provide the correct response.. but not sure if this is correct? I have also found that it is necessary to add a simple AVR model to the dummy ‘G2’ generator to help stabilise the voltage on the islanded system… I assume this is ok, as the standard only talks about excluding the governor? What is considered a ‘pass’ for this study ie what things are you looking to see? | Still under discussion following response from NGESO

## Slide 8: Drafting Modification Update
We have collected about three dozen minor issues that by common consent need to be fed into an update of G99
This is an opportunity to let us know any further minor modifications to the text, or to the forms, which we can propose for the formal change process over the coming winter
Are there any other issues we should include?

## Slide 9: C.6 Dynamic System Monitoring
The informal consultation earlier in the year produced 5 responses
There were a few key suggestions relation to the accuracy classes of instrument transformers, the avoidance of prescription of VT types, and pointing out that our published voltage range for non-effectively earthed systems is inappropriate (principally the 33kV system).
NGESO are reviewing their TS – with the intent of aligning with C.6 as far as possible.
NGESO are also thinking about specifying more detail in relation to the triggering of the detection of low frequency (ie <15Hz) power oscillations – depending on how this develops it might be something C.6 will have to reflect in due course.
NGESO’s changes are governed by the GCRP and will be subject to consultation – probably in Spring 2021

## Slide 10: “Housekeeping” update
All the existing issues are being brought together for an update that we hope to consult on over Xmas
Still an opportunity to raise new points for inclusion – particularly with the compliance forms

## Slide 11: Storage – DCRP/MP/20/06
DCRP WG has now met three times, most recently on 01 October 2020 – and is meeting PM today (03/11)
The drafting of the modifications to G98, G99 and the D Code is practically complete
The work has highlighted the challenges that exist in ensuring EVs operate in vehicle to grid mode (V2G) are compliant – particularly an issue where the inverter is in the vehicle as compliance is determined at charging point, not the vehicle – although this is not really a storage issue per se
The drafting will deliberately suggest that the response to falling frequency below 49.5Hz should trigger a response whereby charging is stopped and generation started. This is anticipation of such a requirement being imposed through the Grid Code in the future.

## Slide 12: G100
DNOs have suggested that:
  The requirements should be recast from first principles rather than include arbitrary limits (eg the 5s tripping time)
  First principles to include considerations such as compliance with P28 – which didn’t exist in current guise when G100 written
  Something fairly prescriptive is required for smaller LV installations; the principles should apply to HV installations, but with less prescription
  Demand management schemes should be included
  Inclusion of demand suggests a revised G100 document for Export/Import control schemes – and probably ideally inclusion in Annex 1 of the Distribution Code
  New challenges like vehicle to grid are included
We are now looking for a first meeting date around the end of November
The issues raised by stakeholders so far are on the next slide – and now is the time to check if there are any other issues to raise.

## Slide 13: Stakeholders’ G100 Issues
No | Issue Description
1 | Password Protection (Apx C. Sec 7) “All . . .settings are password protected and cannot be altered by the customer.” – align with G99 requirements?
2 | Remote Relay from DNO Point of Supply (ELS Design Sec 5) Could occur in a HV connection with a private network in between the generator and POS. Would a comms. link be required? Radio may not work (no line of sight) and you may have to rely on fibre, microwave or TSAT.
3 | G100 is the standard for Customer Export Limiting Schemes, so perhaps a generic standard on the measurement and control of current limiting schemes would be better – which could then equally apply to Export and Import Limitation
4 | Where there are two or more EV chargers one of these will be nominated as the “master” device. This is responsible for measuring the current at the grid connection and reducing the load as required. In our system the “master” device can be a zappi (EV charger) or eddi (power diverter). The “slave” device(s) are connected to each other and the master device using a proprietary 868Mhz wireless link. Once a second, the master device transmits a “power allocation” message to each slave device which then controls its load to match this allocation. If the slave device does not hear the power allocation message of 5 seconds then the output is reduced to zero. Connection from CT to Master Device G100 does not allow for the use of wireless transmitters, this is restrictive as a hardwired connection from the CT to the ‘master device’ is required. The use of ‘Harvi’ transmitters (at 868MHz protocol) could allow for current signals to be sent and the load curtailed if a signal is not received for 5 seconds.
5 | Reverse Power Relays Current fail safes installed operate in 2 seconds but reverse power relays are still required. Some clarification required within G100 document.
6 | “applying G100 principles” to import load curtailment devices would stand some improvement and standardisation. As such, if there’s an opportunity to develop an Engineering Recommendation, I’d be interested to be involved.
7 | Zero export settings are not properly catered for in G100 – it is not possible to set a tolerance on zero
8 | 5s is too restrictive a response time for some technologies

## Slide 14: Brexit and EU Issues
The RfG and DCC (and other Network Codes) are fixed in UK law, and are being modified on “IP Completion Day” to cut the formal references to EU institutions (eg ACER) and processes
The requirements are unchanged
EU Network Code developments. These are not likely to be directly applicable in UK law, but will of course affect the overall EU market, and thus the UK indirectly
Recommendations formally made for changes:
    Storage - RfG and DCC to fully include storage
    Mixed customer sites – all/most Type A and B excluded from the 110kV criterion
In progress:
    Revised/more detailed modelling requirements – should only really affect transmission connexions but the ENTSO-e proposal would allow application for embedded plant (but not Type A)
    Applying Type B requirements to Type A – only concrete proposal so far is to include the active power control port in Type A
    Definition of “material/significant alteration” for retrospective compliance
Entso-e are updating the guidance on compliance – probably still too high level to be particularly helpful (and no longer directly applicable to UK)
50549-10 is likely to be released to national committees and voting in the Spring

## Slide 15: AOB and next meeting
AOB
None
Next meeting
Around the end of December?

## Slide 16
© ENA 2020