## Slide 1: DCRP WG Storage
03 November 2020
Join Microsoft Teams Meeting
020 3855 5885 United Kingdom, London (Toll)
Conference ID: 598 130 995#

## Slide 2: Agenda
Time | Focus | Leader
14:00 | Welcome, Introductions and Acceptance of Agenda | CM
14:10 | Review of Open Actions from Last Meeting | CM
14:30 | Members Feedback on Consultation Paper items Update of draft text of G98 and G99 LF response compliance testing – new G99 drafting V2G Inclusion Members Feedback Update on V2G Status within Consultation Paper Review of consultation paper including all consultation questions Timeline to consultation | SRC MK MW/CM MK MK
15:45 | AOB Date of Next Meeting – suggest w/c 7/12 | MW

## Slide 3: Actions
No. | Detail | Leader | Date | Complete
Action 1 | Write to NGESO | MW | 02/10 | 
Action 2 | Update DCRP on the working group’s progress | MW | 08/10 | 
Action 3 | Provide feedback on draft sketches relating to V2G connection points | ALL | 16/10 | 
Action 4 | Check possibilities of V2G being connected to V1G installation and generating. | SRC | 1610 | 
Action 5 | Arrange meeting with MW and ENA experts on regulatory implications | CM/MW | 16/10 | 
Action6 | Research progress in the EU on these areas | MK | 27/10 | 
Action 7 | Draft appropriate compliance assurance text for frequency response | MK/SRC | 16/10 | 
Action 8 | Raise the possibility of frequency droop for V1G with OLEV/BEIS if possible/appropriate | MW/CM | 27/10 | 
Action 9 | Confirm that the DCRP working group on data exchange is considering storage types | MK | 02/10 | 
Action 10 | Review Marked up copies of G99/G99 and provide feedback | ALL | 16/10 | 
Action 11 | Modify consultation questions 5 and 6 as discussed in the meeting | MK | 16/10 | 
Action 12 | Add a consultation question about the likelihood of <16A V2G | MK | 16/10 | 
Action 13 | Consider if there are any specific frequency response questions that should be included | ALL | 16/10 | 
Action 14 | Propose any further consultation questions | ALL | 16/10 | 

## Slide 4: Status in the EU
From MK 22/10 email:
  I asked ACER (the EU Network Codes regulator) and ENTSO-E what contact they had had with EU vehicle trade bodies etc on the issues of V2G and the proposals that were made to ACER and the EU by the recently concluded Expert Group on incorporating storage into the network codes.
  I think a summary of their answer would be “not much” – but asking them seems to have prompted some action and ACER are setting up discussions on the implications with ACEA, Orgalim and Chargeup Europe. ACER and ENTSO-e are meeting Orgalim Friday 30/10 and Chargeup Europe in the first week in November.
  So it seems we’re certainly not behind Europe in thinking about these things. Although that doesn’t exactly help us.

## Slide 5: Timing of removal of storage exemptions
We are currently drafting amendment 5 to G98 and amendment 7 to G99 take account of the DER tech forum modifications and other updates
We need to remove the storage requirements from a particular date to give notice of the change
There are 3 drafting options for discussion (considered from a G99 perspective):
Option 1
Amendment 7 refers storage users to the specific clauses in Amendment 6 (the storage exclusion clauses)
This EREC applies to Power Generating Modules including Electricity Storage devices commissioned on or after 01 September 2022. Power Generating Modules including Electricity Storage devices commissioned before 01 September 2022 have to comply with with this EREC with the exception of clauses xx, yy, zz and with EREC EREC G99 Issue 1 Amendment 6 clauses pp, qq, rr.

## Slide 6: Timing of removal of storage exemptions
Option 2
Create an Amendment 8 for the storage mods
  This EREC applies to Power Generating Modules including Electricity Storage devices commissioned on or after 01 September 2022. Power Generating Modules including Electricity Storage devices commissioned before 01 September 2022 have to comply with EREC G99 Issue 1 Amendment 7.
  This means amendment 7 will need to be closely followed by an amendment 8
Option 3
Cover both the DER and storage mods in amendment 7
  This would mean several sets of text in several paragraphs and double sets of drawings with time limited applicability.
  This is the least readable option

## Slide 7: Significant drafting changes
The most recent (end October) circulation of the drafts of G98 and G99 modified for storage have the following significant changes to note (marked in documents using track changes as “ENA2”):
Modification of foreword – new requirement to switch from import to export under severe frequency event
New definition:
  Vehicle to Grid Electric Vehicle - An electric car and any associated internal or external charging devices that can import electricity from and export electricity to the Distribution Network.
V2G earthing figures moved to Section 8 and simplified figures included in Section 6 – see slide
Some tiding up of words in respect of frequency response and revised diagram for Type A, B and C&D requirements– see slide
Compliance testing – references included in Form A2-1, A2-2 and A2-3 as well as the PGMDs for Type B, C & D
Compliance test proposals included in Annex A.7.1.7, A.7.2.3.2, B.5.4, B.6.3, C.8.8 and C.9.6 – see slide 11

## Slide 8: Simplified figures 6.10 and 6.11
With V2G capability on the car and with V2G capability in at the customers installation
Connexion Point
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)

## Slide 9: Storage response frequency requirements (eg) para 13.2.3.3
A Power Generating Module that incorporates an Electricity Storage device, must be arranged to automatically respond to falling frequency in line with the characteristic of Figure 13.2 until the stored energy is depleted.
The required characteristics are:
When the frequency falls to 49.5 Hz the automatic response should start;
The frequency response characteristic is to be within the shaded area of Figure 13.2
If the Electricity Storage device is not capable of moving from an import level to an appropriate export level within 20 s of the frequency falling to 49.2 Hz, then it should be tripped; and
If the Electricity Storage device has not achieved at least zero Active Power import when the frequency has reached 48.9Hz it must be tripped immediately.

## Slide 10: Revised diagram for falling frequency (eg figure 13.2)

## Slide 11: Compliance of falling frequency response
Generic approach for all Types:
The Generator will propose and agree a test procedure with the DNO, which will demonstrate how the Power Park Module Active Power output when acting as a load (ie replenishing its energy store) responds to changes in system frequency.
In general four tests are proposed, one set of two at Registered Capacity in import mode, and one set of two at 40% of import Registered Capacity.
In both cases the test is to reduce frequency from 50Hz at 2Hz s-1. In the first case the lower frequency reached will be 49.0Hz and the second case the lower frequency will be 48.8Hz.
In all cases the response should meet the requirements of [11.2.3.3]
The above has been shared with NGESO, who have indicated that this seems appropriate

## Slide 12: V2G
Following on from ENA’s email the suggested position is:
We should include all likely/expected requirements as applying to V2G
Need to ensure the consultation reaches out fully to the EV manufacturing community
DNOs are reviewing their EV and V2G experience to date and will see if it is appropriate to ask further specific questions in this area

## Slide 13: Consultation Paper
Modifications since last meeting
Mainly editorial
Clarity that we are requiring the new droop characteristic on falling frequency (ie switch from charge to discharge)
Questions revised

## Slide 14: Current Questions:
Do you agree with the general intent of the proposed modification? If not, please explain your views.
Do you agree with the approach to a timed future implementation and do you agree with the suggested date?
Do you agree that the data requirements relating to storage technologies etc should be left to the DCRP working group on data exchange provisions to resolve?
Do you agree with the general approach taken to V2G requirements? If not, please state what you think is incorrect and inappropriate and please suggest any alternative approaches.
Do you foresee that V2G will be needed for EVs of under 3.6kW registered generating capacity? If so, this would require appropriate drafting to be included in G98.
Do you agree that DNOs should insist on formal Equipment Certificates for vehicle manufacturers to demonstrate compliance of V2G capabilities? If you disagree, please explain why.
Do you agree with the inclusion of mandatory cessation of active power, and change to generating mode, on falling frequency and do you agree with the thresholds suggested? If you disagree, please explain why
Do you have any comments on the proposed legal text drafting?
Do you have any other comments?

## Slide 15: Timeline

## Slide 16: AOB & date of next meeting

## Slide 17
© ENA 2020