## Slide 1: DER Technical Forum
21 September 2021
14:30 start
Microsoft Teams meeting
Join on your computer or mobile app
Click here to join the meeting
Or call in (audio only)
+44 20 3855 5885,,657084549# United Kingdom, London
Phone Conference ID: 657 084 549#
Find a local number | Reset PIN

## Slide 2: Welcome, Housekeeping and Introductions

## Slide 3: Agenda
1 | 14:30 | Welcome, Introductions and Acceptance of Agenda.
2 | 14:35 | Special Interest Session on Modelling/Simulations
3 | 14:45 | Technical issues surrounding BESS connexions
4 | 15:15 | New Issues since the last forum: Heat batteries
5 | 15:15 | Unresolved issues 112, 114 & 115
6 | 15:30 | G100 review – update
7 | 15:35 | Fast track review - update
8 | 15:40 | Distributed Restart
9 | 15:45 | EU Developments
10 | 15:50 | D Code compliance developments
11 | 15:55 | AOB
12 | 16:00 | Next Meeting Arrangements

## Slide 4: Special Interest Session on Modelling and Simulations

## Slide 5: Modelling and Simulations
4 definite expressions of interest.
Proposed agenda shown here.
Open to other suggestions for the agenda.
Open for other attendees.
Suggest a date around the end of October.
1 | 00:00 | Welcome, Introductions and Acceptance of Agenda.
2 | 00:05 | Requirements in G99 History RfG and current requirements
3 | 00:20 | DNOs’ software etc requirements
4 | 00:35 | IPR and NDAs etc
5 | 00:50 | Common assumptions: Fault levels Background harmonics etc Ramp rates etc Power factor ranges/requirements Voltage control modes, tap positions etc
6 | 01:40 | Machine data: Reactances Time constants Inertia Control systems/settings
7 | 02:00 | Interpretation of study results
8 | 02:35 | Implications of GC0141
9 | 02:45 | Actions
10 | 02:50 | AOB

## Slide 6: Battery Energy Storage Systems

## Slide 7: There are a number of issues associated with BESSs
Issues identified:
  Voltage step changes.
  Operating power factors and reactive contributions.
  Switching from quiescence to full output or import versus switching between full output and import.
  Frequency of operation, and hence voltage step changes.
  Allocation of upstream capacity.
  Aggregation of BESSs which are close (electrically) together.
  Uncertainties over exact modelling approach.
  Are there any more?
DNOs are actively now discussing how to harmonize their approaches, as well as recognizing the need to accommodate new BESSs readily and inexpensively.
DNOs suggest that this topic be discussed in detail at a future DER TF, as soon as possible, ideally in November.

## Slide 8: New Issue

## Slide 9: Heat Batteries
Q - Caldera’s technology is a domestic heat storage device. There is some confusion amongst DNOs’ connexions department as to how to treat it, including suggesting that it should be applied for using the G99 application forms.
A - Only energy that is converted in a cycle of electricity-storage-electricity is in scope of G99 – the definition is:
  Electricity Storage
  Electricity Storage in the electricity system is the conversion of electrical energy into a form of energy which can be stored, the storing of that energy, and the subsequent reconversion of that energy back into electrical energy.
As the heat stored in Caldera’s technology cannot be converted back to electricity, it is not within the scope of G99.
Recognizing that it is a significant new load that should be discussed with the DNO prior to installation it would make sense to be applied for on the most appropriate form. Currently it seems that the heat pump application form is the most relevant and we recommend using this for the time being.

## Slide 10: Previous Issues

## Slide 11: Unresolved previous issues - 1
No | Issue | Assumed Status
110 | There is uncertainty over the detail which needs to be submitted for type C and D compliance simulations – particularly the supporting information about the models which could be considered to be the consultants’ IPR. | Although simulations and their models have been discussed several times, and there are a few entries in this log, it might be worth holding a review of what is considered to be appropriate good practice in this area with appropriate stakeholder and DNO experts. Stakeholders will be canvassed to gauge interest in a dedicated session to develop this.
112 | A common issue that keeps coming up is Registered Capacity vs design install and grid agreements. I have a specific case where the G99 and connection agreement is for 9MW, the developer undersized the inverters slightly. So it can only produce 8.5MW ( in round numbers) whilst operating in the 0.95 lag/lead range. This is what is shown when we do the G99 study, and we noted this shortfall. So the question arises, of what happens to the site now and what can it do. Specifically, 1) Is it’s new official RC 9MW or 8.5MW I.e do they retain their original agreed capacity, or is this list back to the DNO? This is a common sticking point, taking the above example it cannot meet the 9MW required, but they may upgrade an inverter later to give them more MVAr headroom and it could then operate at 9MW. 2) If the DNO doesn’t want/need them to operate across the 0.95 lag/lead range can they then operate at 9MW active power and say unity or 0.98pf. In this case they are producing their official R, but their system design does not meet the required G99 standard for a 9MW site. | This is an issue that does re-appear from time to time. We have attempted to deal with it in the past in issues 40, 80 and 83. We went through it with slides at the 7 June DER TF. DNOs have summarized how they specify maximum capacities and power factors in their connexion agreements (see next slides) We propose that we incorporate the material from the 7 June into the next version of the DG guides.

## Slide 12: DNOs standard formulation of maximum import/export limits - 1
Northern Powergrid
UKPN
SSE
Voltage | Import |  | Export | 
 | VA or W | PF | VA or W | PF
EHV | kVA | Defined in agreement Generally allowed to be in the range unity to 0.95 lagging. In certain cases fixed in the connexion agreement to a narrower range or specific PF | kW or kVA | Defined in agreement Generally allowed to be in the range unity to 0.95 lagging. In certain cases fixed in the connexion agreement to a narrower range or specific PF
HV | kVA | NTC* | kW or kVA | NTC*
LV |  |  |  | 
Voltage | Import |  | Export | 
 | VA or W | PF | VA or W | PF
EHV | kVA | Defined in agreement (default unity) | kVA | Defined in agreement - default 0.99 leading
HV | kVA |  |  | 
LV |  |  |  | 
Voltage | Import |  | Export | 
 | VA or W | PF | VA or W | PF
EHV | kVA | Defined in agreement | kVA | Defined in agreement
HV | kVA |  |  | 
LV |  |  |  | 
*National Terms of Connexion

## Slide 13: DNOs standard formulation of maximum import/export limits - 2
WPD
Electricity North West
SPEN
Voltage | Import |  | Export | 
 | VA or W | PF | VA or W | PF
EHV HV | kVA | To be in the range 0.95 lag to unity. | kVA | Defined in agreement
LV |  |  |  | Unity - but within the range ±0.95
Voltage | Import |  | Export | 
 | VA or W | PF | VA or W | PF
EHV | MVA / kVA | Defined in agreement Generally allowed to be in the range unity to 0.95 lagging. In certain cases fixed in the connexion agreement to a narrower range or specific PF | MW / kW | Normal operating pf defined in agreement (default unity pf) Also state that generators >1MVA must be capable of operating in the +0.95pf (lead/lag) envelope
HV | kVA | NTC* | kVA with kW and pf | Normal operating pf defined in agreement (default unity pf)
LV |  |  | kVA | NTC*
Voltage | Import |  | Export | 
 | VA or W | PF | VA or W | PF
EHV | kVA | Defined in agreement. SPD default is in the range 1.0 to 0.90 lag. | kVA | SPD: voltage control mode. SPM: default unity to 0.95 lead but averaging to unity. Lagging PF not allowed with prior permission.
LV |  | NTC* |  | Not defined

## Slide 14: Unresolved previous issues - 2
No | Issue | Assumed Status
113 | P28 has the usual classifications of frequent events, infrequent events (4 per month) and very infrequent events (1 per 3 month)…. what should we be assessing a storage system performing a dynamic containment service as? The UK grid is reasonably stable, at the moment, but with more conventional plant dropping out, the power swings are going to get a bit more sever, and the DC type services will be getting worked more often. Classing it as a very infrequent event probably isn’t realistic, but what about infrequent events? I could see that it is possible that you could get to around the 4 events per month, although probably not at the full power swing. | This is a good point, and one that probably would benefit from a consistent consideration by DNOs. It might be sensible to base the frequency on the observed incidence of frequency excursions, over the last 18 months say, that trigger a specific level of response from such services. The response level might be set locally, and the P28 “frequency of event” set by the historic track of frequency excursions triggering that level of response. This can be calculated from the information NGESO publish monthly This should be picked up as part of ongoing work to develop a common approach to BESSs between the DNOs.

## Slide 15: Unresolved previous issues - 3
No | Issue | Assumed Status
114 | We have concerns relating the voltage step change for Battery Energy Storage Systems (BESS) when the systems are designated for fast frequency response. A number of network operators define step change to be full declared export to full declared import for real power P and for reactive power Q. The FFR contracts do not have a contracted obligation to reverse the direction of reactive power flow and no obligation to match the fast MW response with a MVAr response. When importing, there is no obligation to operate at a particular power factor only to operate within a +/-0.95 range. If a full MW ramp has occurred, it is reasonable to assume the system is under stress. To reverse Q at this point would be the worst of all strategies at it would exacerbate the stress of the system by introducing an unnecessary voltage step. It is likely that EFR or FFR BESS is located at a point with a high X/R ratio (close to a BSP or GSP). Therefore a unit change in Q would have at least 10x the impact on at the voltage step that of a unit change in P. This Q reversal condition appears to be based on a false assumption about the default behaviour of inverters under FFR. We believe it is a matter for the customer to demonstrate through simulation the voltage step change under power reversal. It is a matter for the customer to produce a reactive power strategy that meets the constraints of the D Code and the connection offer. Confirmation of the simulation can be done via commissioning tests with frequency injection for smaller steps. The imposition of this requirement distorts the market by essentially limiting the capacity of a BESS scheme to around half the capacity of other technologies thus creating hidden barrier to the penetration of the technology. The customer should demonstrate how they meet the voltage step change challenge through modelling and if necessary to verify through commissioning demonstration, not for the network operator to impose a control philosophy. | Currently being review by DNOs

## Slide 16: Unresolved previous issues - 4
No | Issue | Assumed Status
115 | There is some ambiguity of the treatment of induction generators under G99. Typically these generators are used in hydro schemes, but they are also on steam turbine applications. The systems are asynchronous thus do not qualify as a synchronous generation module. The only other qualification would be as Power Park Modules. Paraphrasing G99, PPM are devices that may control one or more asynchronous generators. It seems that this statement includes a tacit assumption that the asynchronous machines are controlled by the PPM, ie an assumption that they have individual PQ control as is the case with a static inverter system. A single induction machine however has no mechanism to control frequency (it is asynchronous and operates at a slip speed against the system frequency). It has no voltage control as the field is induced by the rotor slip speed against the rotating stator field. A distinction between an induction generator and a static inverter or DFIG is made in the current version of G59 where the 0.5s definite ROCOF requirement is waived specifically for induction generators [10.5.7.1]. This actually makes sense as an induction generator can generate severe overvoltages if its speed increases while connected in island through a longer cable. The same clarity is not present in G99 however. It is unclear to some network operators how to categorise these devices. We believe the current WPD practice toward these schemes (evidenced through their treatment of numerous Hydro schemes) is the correct interpretation. Unfortunately, this does not seem to be a global interpretation. We therefore suggest inclusion of some clear statements within G99 that clarify the exclusion of induction generators form the type test, simulation, and support (ie voltage reactive fault ride through etc.) ie distinct from the requirements for PPM with PQ controlling static generators and synchronous generators. These are services that an induction machine cannot supply by definition. | The exception in G59 10.5.7.1 is a relaxation for existing installations that are unable to modify existing equipment to implement the current loss of mains requirements. Loss of mains (LoM) protection is principally to prevent power islands forming in the DNO’s distribution system. It is not intended to guard against undesirable effects in the generator’s installation. The relaxation is allowed for historic installations because the analysis undertaken by the joint DCRP and GRCP working groups GC0035 and DC0079 established that the risk of islands being sustained by any technology was acceptably low, when considered across GB, with the exception of synchronous and DFIG machines, which have greater natural ability to support islands. Of course, the disablement of LoM protection leaves the G59 required frequency and voltage protection in place – and these remain essential as part of the defence against islanding. This relaxation relieves the generator from having to invest in new LoM protection for those installations where the existing LoM protection was not capable of being set to the current requirements. It is not appropriate to add to the risk of islanding, seen across GB, by allowing new installations to be commissioned without LoM protection. LoM protection does not have to be RoCoF – although VS is no longer allowed, which does limit the options. Induction generators are defined in primary legislation to be Power Park Modules. A Power Park Module is defined as all the equipment necessary to meet G99’s requirements (which are just a reflection of the primary legislation) – so apart from the induction machine(s) there might be a need for reactive compensation equipment, and the appropriate control equipment, such that all of the relevant G99 requirements are met. There is no scope excepting any Power Park Module, of any technology, from the requirements of G99 unless a derogation is sought from Ofgem.

## Slide 17: Update G100 review

## Slide 18: G100
Last formal meeting 08 September.
Consultation produced very effective input from 7 stakeholders and 2 DNOs.
Most responses contain a mix of strategic issues and specific points of detail.
The strategic issues relate principally to the development of demand side services in Great Britain, and the possibility of G100 having adverse interactions here.
In particular:
  Excessive mode 2 excursions counterproductive as drafted.
  Need to not hinder the development of EV smart charging (EV Energy Task Force)
  Queries re PAS 1878 and 1879 development and adoption by the wider industry
  Approaches to cyber security and EN303 645,
Key outcome of the 23/07 WG meeting reviewing the above was agreement to allow 5s excursion into mode 2 before classing as an excursion counting towards excessive excursions.
Modes renamed as States.
A second consultation planned for mid October, of 8 weeks.

## Slide 19: Fast Track
Broad DNO agreement on lifting the export limit to 32A total generation, or up to 60A if G100 limitation scheme employed to limit export to 32A.
Existing fast track criteria still exist – so aggregate generation <32A and a G100 scheme set to 16A has automatic acceptance of the application within 10 days.
The new proposed fast track will subject applications to a triage process within 10 days. Most will easily pass, but some, where the system is weak, will need normal formal assessment and quotation.
The triage process will allow for other considerations, such as local saturation, to be considered.
The next planned formal stage is to present the proposed modification to G99 to the October DCRP.

## Slide 20: Distributed ReStart Project

## Slide 21: Distributed Restart Project -1
Introduces the concept of an Anchor Generator, which is an embedded PGM cable of self starting and re-energising the DNO’s system, supplying DNO’s customers, and ideally being able to re-energize an element of the transmission system.
The Project’s working assumption is that such PGMs might be as small as 2MW, but in all cases would be required to accede to the CUSC.
The draft requirements are being incorporated into Grid Code OC9 (black start) and OC5 (testing).
If all formal participants of a distributed restart zone (DRZ) are CUSC parties, there is arguably no overwhelming need to place requirements in the D Code. However, in both the interests of not limiting the approach to CUSC parties, and transparency and clarity, it seems highly desirable to create harmonized requirements in DOC9 and DOC5.

## Slide 22: Distributed Restart Project - 2
The Project currently intends to use GC0148 (E&R Implementation – a joint GCRP/DCRP WG) to introduce the Grid and Distribution Code modifications – although this might not happen if the DRZ drafting is too much scope creep for GC0148.
NGESO also have to respond to their new Electricity System Restart licence condition, which might lead to a change of status and ambition for the project.
NGESO has mentioned the touch point too with GC0117 in terms of where an embedded PGM will become Large in future.
G99 largely avoids direct conflict with DRZ requirements, but would benefit from a few tweaks (particularly to the definition of its scope) to remove any possible confusion.
The project has captured its first thoughts on drafting of the Grid Code, D Code and G99 and will be fed into the formal consultations of GC0148.

## Slide 23: EU Developments

## Slide 24: 3 key developments
The Expert Groups will deliver their final reports to the European Stakeholder Committee on 22 September.
Potentially these will feed into updates to the network codes – so not likely to be primary legislation in the UK
  Baseline for Type A generators
    TSOs want fault ride through for all type A
    DNOs (and manufacturers) want greater clarity and harmonization on certification
    DNOs and TSOs want Type B controllability rather than just an off-switch
    All the above might be excepted for μCHP and CHP (and other specific technologies) ≤ 50kW
    Not proving easy to turn all this into a report.
  Criteria for Significant Modernization
    Will recommend that thresholds for key electrical characteristics (eg 50% increase in registered capacity) trigger full compliance.
    Might provide useful clarity; might be ineffectual (depending where the thresholds are set).
  Interaction Studies and Simulation Models
    Additional modelling options for TSOs to impose on Type C and D generators, and for new distribution systems (no such thing) and facilities (GSPs)
    Currently unclear if these will be mandatory on embedded generators, or at DNO discretion
    NGESO not represented and do not seem interested - probably because their interests are being developed in GC0141

## Slide 25: Distribution Code Compliance

## Slide 26: Distribution Code Compliance
Background:
  The accelerated loss of mains programme requires that all generation in GB retrospectively adopts new loss of mains protection arrangements.
  In some cases these changes are not trivial.
  In some cases owners might ignore the requirements.
  DNOs have not had a strong historic need to rigorously enforce D Code compliance, and lack the legal tools and experience to routinely challenge non-compliances, both in general, but specifically for loss of mains protection.
Solution
  Modification DCRP/21/05/PC proposes D Code text that works through a managed compliance process over six months.
  Subject to appropriate checks and balances, if compliance not achieved in this timescale, the customer can be disconnected by the DNO.
  Consultation closes on 7 October.

## Slide 27: Wrap up:

## Slide 28: Minutes of previous meeting and actions
Outstanding matters arising not on the agenda:
  None?

## Slide 29: AOB and next meeting
AOB
None?
Next meeting? Around the end of November?

## Slide 30
© ENA 2020