## Slide 1
DER Technical Forum
29 March 2023
10:00 – 12:00
Microsoft Teams meeting

## Slide 2: Welcome, Housekeeping and Introductions

## Slide 3: Agenda
1 | 10:00 | Welcome, Introductions and Acceptance of Agenda.
2 | 10:05 | Update on BESS issues
3 | 10:20 | New Issues Examples for G99 A.6 (Ian Nicoll)
4 | 10:35 | Update on existing issues
5 | 10:50 | Areas for update/inclusion in the DG Guides
6 | 11:00 | Update on G100
7 | 11:15 | Prototypes
8 | 11:25 | Other Updates GC0117 - extension of Grid Code to embedded generation GC0156 – electricity system restoration standard EU developments
9 | 11:35 | AOB
10 | 11:40 | Next Meeting Arrangements

## Slide 4: Battery Energy Storage Systems

## Slide 5: BESS stakeholder meeting
Most recent meeting was held 28 March 2023
High level process diagrams of the BESS application process were shown for each DNO – it was agreed that these would be more useful if they captured the distinction between BESSs with and without frequency response contracts – DNOs agreed to do this.
In discussing the effect of frequency contracts on voltage step change, stakeholders made the point that frequency events themselves were not monotonic ramps or steps in reality (and were slow to the extent they were limited by the system inertia) and therefore didn’t match the assumptions in P28 for step changes. DNOs agreed to consider this and noted that some of these points would naturally fall into the interpretation of P28.
It was also noted that the DCRP has agreed to review P28, with a view to providing the sort of interpretation suggested above.

## Slide 6: New Issues

## Slide 7: New Issue
Not really a new issue – but a reminder to include issue 111 in the list of updates for a future issue of G99:
Do new connexion arrangements to an existing generation site trigger retrospective compliance of the existing generation on the site with G99? | For the example described, where the site is in the same ownership, and the power generating module is unchanged, there is no reason to consider retrospective applicability of G99. This case does not trigger any of the three key criteria for retrospective compliance; namely it does not meet the legal need of the RfG (ie it is not a Type C or D installation), it does not meet the long standing GB driver of significant investment in the power generating module and the electrical characteristics of the power generating module are unchanged. It might be worth adding this example to Appendix A.6 in the future.

## Slide 8: Previous Issues

## Slide 9: Outstanding Issues:
Delays associated with DNOs being able to submit Mod Apps to NGESO because of inadequate SAF data – 126
Initial P28 assessments for generation tripping and/or load rejection etc. – 127
Older issues – included in the annex.
  Registered Capacity – 112
  BESS connexions – issues 113, 114
  Cybersecurity – 117 – to follow up with AMPS
  Classification of PGMs – 121 – to follow up with AMPS
  5 minutes per month for STP – 122

## Slide 10: Recent outstanding Issues – 1
No | Issue | Current Status
126 | Customers are still seeing very long delays for DNOs to submit a Modification Application to National Grid for the appropriate GSP. A developer accepted a scheme Sept 2020 and only had the Mod App response back August 2022 (even with pushing for a Mod App to be done with escalation). This is not an isolated experience. One part of the delay occurred as the DNO informed us they are allowing customers to only fill in sections 1 -3 before receiving a distribution offer, but required customers to fill in section 4 before they were able to submit the Mod App. Whilst the customer UBGC represented had filled in Part 4 when the scheme was applied for, others which accepted before had not and a Mod App was further delayed, to allow customers who accepted ahead to fill in the form. This would have been 14+ months after they had initially accepted their offers. If Part 4 is a requirement for a Mod App but the DNO feels comfortable making a distribution offer without part 4, can it be agreed that part 4 it is filled in within a set period, I.e. 2-3 months of acceptance to prevent further delays in Modification Applications in the future or that the Mod App is submitted based only on the information within parts 1-3. | The timing of the provision of data is prescribed in DPC1 of the Distribution Code – needs review to see how this suggestion might be accommodated. Need to set up some discussions with appropriate DNO experts as soon as possible. Following a meeting between Philip and DNO experts from NGED and Electricity North West it is suggested that Part 4 of the SAF becomes mandatory.

## Slide 11: Recent outstanding Issues – 2
No | Issue | Current Status
127 | There is a requirement in ENA P28/2 (Although fairly sketchily defined) that we are supposed to consider what happens if a generator trips under full load conditions at different power factors ie 0.95 lag, unity and 0.95 lead. We have had a fairly large number of these sites come up that have a problem on them, and when we carry out the studies, we get a fail (ie the SVC is greater than +/-3%). When we hit this point there isn’t really much we can do to help, as the SVC results are really just a function of the MW, MVAr flow and system strength – the only option is to constrain the generator MW output if it is at a problem PF – this causes headaches for developers Some general thoughts would be A generator tripping on full load conditions would be relatively unusual – although with G99 LoM protection I guess it can and does happen, so I can see why its there. Is it really realistic to consider it against minimum (outage) fault condition? Should the developer really be doing this and finding problems - it is such a simple assessment the DNO should really do this, and check before issuing an offer. In reality just a simple loadflow of before and after. | DNOs broadly agree that the DNO should undertake these checks early in the application process. It is appropriate (and necessary in P28) to consider outages. To be investigated further as part of the refinement of BESS processes.126.

## Slide 12: DG Guides

## Slide 13: DG Guides 2023 Annual Updates
Updates in accordance with industry developments
Proposed content to update:
What is missing?
Chapter A
Revisions needed to remove ‘traditional’ network terminology and update to reflect the GB network in 2023
Chapter B
Section dedicated to Distributed Generation. Requires an update to reflect current landscape
Registered Capacity
Revisions to the definition of Registered Capacity and inclusion of suite of examples is needed
Ofgem Significant Code Review
Updates needed to reflect the new rules for charging generator developers for new connections
ENA Open Networks Project
Updates needed to reflect latest developments from the Open Networks Project
Storage and V2G
Review current content on both topics and take account of the recent SAF changes on voltage step change assessments
Flowcharts
Update existing flowcharts or the inclusion of a new chart to guide users to the appropriate relevant documentation to complete
Non-firm connection
New section in the Guides to discuss receiving non-firm connections to curtail generation output when reinforcement is necessary
On-line SAF
e.g. UKPN Smart Connect Portal

## Slide 14: Changes to the presentation and layout of the guides
Consideration of changes to the presentation have been proposed
Any change is subject to approval by the DNOs
  Combine the current versions of the DGCGs into a single document
  Consideration will be made on the appropriate material to include in the document that is applicable for both G98 and G99 readers
  An additional option is being proposed to move the current material from Microsoft Publisher to a Microsoft Word document
  Two column format less suitable for online viewing – revert to single column
Discussion
Further comments by 3rd April

## Slide 15: Update on G100

## Slide 16: G100
Issue 2 Amendment 1 has been published on 25 July last year.
In the intervening period, several stakeholders have made representation to the ENA about various implications of the draft.
In response, the DNOs have proposed to:
  Remove all voltage triggers for state 3 – considerably simplifying several aspects of the requirements;
  Include guidance for high diversity installations – such as massed EV charging points;
  Harmonize all detection and response times within a CLS to 15s
  Remove the necessity of a state 3 response for the comms loss to a single device
  Clarify the implementation date (01 May 2023)
This revised version is undertaking internal ENA sign off and should be published around the middle of April.
A stakeholder briefing session is being arranged for Thursday 13 April.

## Slide 17: Prototypes

## Slide 18: Prototypes: compliance
An issue was raised (albeit not formally) by a manufacturer some time ago in relation to the challenges of agreeing a legal connexion of a prototype where manufacturer’s information would not be available at the time of commissioning.
Although we had expected this issue to arise some time, in reviewing the implications it now seems that there should be no issue.
Our current view is that:
  For type A, everything that needs to be demonstrated etc can either be done on site with the prototype or can be demonstrated on a grid simulator;
  PGMs larger than type A can use the ION/FON route, albeit unofficially for Types B and C, until sufficient information has been gathered from prototype operation and when simulations have been verified.
Accordingly DNOs do not think there is a need to make any specific accommodations in G98/G99 for prototypes.
Does the Forum agree?

## Slide 19: GC0117

## Slide 20: GC0117 – alignment of Large, Medium and Small across GB
The WG consultation closed on 05 August:
  Out of 14 respondents, 3 support the original proposal (ie 10MW Large threshold throughout GB) and 3 support the WAGCM1 proposal (ie 100MW threshold). Some believed that the solutions had not been sufficiently fully developed. Others believe that a CBA and further investigations are required to fully assess the proposed solutions against the applicable Grid Code objectives.
  Some respondents expressed that the rationale / case for change is not clear. No demonstration of how the change would simplify and align Grid Code and generation considering discrepancies identified.
  Majority of respondents agreed that it is appropriate to change the definition of Demand Capacity and associated Grid Code definitions to align with the changes to Large, Medium and Small Power Stations but, via a separate modification.
  Most respondents were in support of revising the definition of Registered Capacity.
  Most respondents do not support a retrospective approach as it will be complex and result in increased costs.
  Majority supported establishing a holistic view of the required future net zero arrangements of the technical and commercial arrangements for connecting new and operating existing and new generators.
  A respondent advised that a holistic review is already being taken forward by the Open Networks project and continuing with GC0117 could result in duplication of effort and recommendations contrary to proposals under Open Networks.
This is being developed quite slowly, with the current activity focusing on NGESO creating a cost-benefit analysis (CBA). NGESO were only intending to cover NGESO costs and benefits, but Ofgem has advised that the costs and benefits for all affected parties must be included. It is not clear how NGESO will achieve this and they held a WG meeting about this on 08 December.
Further CBA meetings are currently in progress.

## Slide 21: Distributed ReStart: GC0156 Electricity System Restoration Standard

## Slide 22: Electricity System Restoration Standard – GC0156
Distributed Restart is now being progressed as part of the wider ESRS implementation in GC0156
GC0156 formal working group consultation closed on 29 December.
Matching D Code drafting was consulted on from 12 December 2022 to 13 January 2023.
As a result of the consultation responses the legal text of the Grid Code has been substantially modified, the Distribution Code less so, but it has nevertheless changed somewhat.
The Grid Code text will be consulted on again during May and, subject to the DCRP agreement, the matching Distribution Code text may also be consulted on at about the same time.
Interested DNO stakeholders should review the D Code drafting to ensure they understand the obligations on those who might wish to contract for Restoration Services.

## Slide 23: EU Developments

## Slide 24: EU Update
All of this is not expected to have a direct effect on GB; however it will influence the wider market GB operates in.
ACER is now consulting on revisions to the RfG and DCC.
As expected, issues such as the inclusion of storage, and the revision of the Type D voltage threshold seem widely supported.
V2G is a rapidly developing area, and ACER are contemplating divorcing the requirements for EVs from Type A generation. In particularly they are currently proposing:
  Compliance demonstrated purely by a certificate up to 2.4kW
  Identical exhaustive requirements across the EU (ie for V and f ranges, LFSM-O, LFSM-U, FRT)
ENTSO-e are arguing that from 3 years hence all inverters/converters should be grid-forming, although stakeholders and ACER currently seem to think this is premature.

## Slide 25: Expert Group Reports:
Offshore Connexion Requirements.
  Interesting to note that report will also now pick up the integration of issues like hydrogen production, electrolysis, power to gas etc.
Harmonization of Product Family Grouping and Acceptance of Equipment Certificates in European Level
  This is a big report and requires some digesting and it’s only just now been delivered. However, ACER has asked that the EG now produce some draft legal text to implement the recommendations in RfG 2.0. The EG has accepted the challenge but in the discussion it does seem that to fully implement the recommendations, changes to law other than the RfG might be required.
  The main components of the report are attached on the next slide. There could be some useful recommendations which might have beneficial application in GB or the UK.
Advanced Capabilities of Power Park Modules
  This is not quite finished – it is somewhat controversial and it is clearly interactive with the grid forming proposals from ENTSO-e, although ENTSO-e are not very involved in the EG. The report is expected to be finished in late March and ideally will include some draft legal text. The legal text includes variations as preferred by different stakeholders (eg TSOs, generator manufacturers, DSOs etc).

## Slide 26: Harmonization of Product Family Groupings and Equipment Certificates
PGU vs PGM
  PGU certificates can be harmonized at EU level
  These PGU certificates may cover specific (national) grid codes, more generic grid connexion requirements (NC RFG, EN standards) or simply the PGU’s outmost capability
  PGU certificates can be used within the process specified in the NC RfG to demonstrate compliance at the PoC
  TSO/DSOs will keep the right to require additional compliance simulations or on-site compliance testing.
EG HCF didn’t identify a standardized approach for PGM compliance
  This could be achieved either through a certification process at PGM level using the PGU certificates, or by accepting a PGMD (or similar document) coming from a PGF owner based on the content of the PGU certificate and additional site-specific testing and simulations.
The implementation of PGMDs (or similar) can be the key link between PGU compliance assessment at PGU terminals (PGU certification) and the PGM compliance in regard to the PoC.
  PGMD definition in the NC RfG is restricted to type B and C. It is recommended to create new expert groups and extend the PGMD concepts to type A and type D. The complexity of PGMDs is based on national definition and PGM size.
Family definition applies to a group of related products that shared common characteristics or features coming from the same manufacturer
  Includes common points that define the family and must be included
  Transferability of test results can be done within the family
  EG HCF suggests having a family definition per design technology which is manufacturer based, regardless of power range and voltage level

## Slide 27: Harmonization of Product Family Groupings and Equipment Certificates - 2
Simulation model is a KEY tool to evaluate PGU and PGM performance
  Reduce amount of test permission applications to relevant SO and reduce test disturbances to grid
  A validated model using existing quantitative methodologies (very stringent) provides a high level of fidelity and allows better understanding of the FRT performance of the unit.
  The model shall correctly represent the structure of the unit and shall be validated against test results.
  This model shall be used with the overall facility simulation model which shall correctly represent the structure of the system/module/unit including the system parameters.
Formal requirements on PGU certification
  Unambiguous reference to certification programmes that are accepted by the RSO
  Clear definition of specified requirements that are accepted by the RSO
Umbrella certification is the most promising approach for harmonization of PGU certificates.
  Certification on EU level may be provided by a “capability certificate” that can easily be enhanced by grid code specific conformity statements.

## Slide 28: Other EU items - 50549
EN 50549-10 was published in the middle of November – although another review iteration is already supposed to have started in which case another version might appear in 12-18 months time.
Work to progress urgent and minor proposed amendments to 50549-1 and 2 is on course to go out to inquiry to member states standards bodies by the end of March 2023.
Depending on the ACPPM reported above, CENELEC will consider the implications along with harmonizing to the prospective 50549-1 and 2 in April. CENELEC are also proposing to start a new expert group to standardize grid forming requirements – but this has yet to be formally agreed.

## Slide 29: AOB and next meeting

## Slide 30: Appendix – historic Forum issues

## Slide 31: Outstanding Issues – 1
No | Issue | Assumed Status
112 | A common issue that keeps coming up is Registered Capacity vs design install and grid agreements. I have a specific case where the G99 and connection agreement is for 9MW, the developer undersized the inverters slightly. So it can only produce 8.5MW ( in round numbers) whilst operating in the 0.95 lag/lead range. This is what is shown when we do the G99 study, and we noted this shortfall. So the question arises, of what happens to the site now and what can it do. Specifically, 1) Is it’s new official RC 9MW or 8.5MW ie do they retain their original agreed capacity, or is this list back to the DNO? This is a common sticking point, taking the above example it cannot meet the 9MW required, but they may upgrade an inverter later to give them more MVAr headroom and it could then operate at 9MW. 2) If the DNO doesn’t want/need them to operate across the 0.95 lag/lead range can they then operate at 9MW active power and say unity or 0.98pf. In this case they are producing their official R, but their system design does not meet the required G99 standard for a 9MW site. | This is an issue that does re-appear from time to time. We have attempted to deal with it in the past in issues 40, 80 and 83. We went through it with slides at the 7 June 2022 DER TF. DNOs have summarized how they specify maximum capacities and power factors in their connexion agreements. We propose that we incorporate the material from the 7 June 2022 meeting into the next version of the DG guides

## Slide 32: Outstanding Issues – 2 – in progress
No | Issue | Assumed Status
113 | P28 has the usual classifications of frequent events, infrequent events (4 per month) and very infrequent events (1 per 3 month)…. what should we be assessing a storage system performing a dynamic containment service as? The UK grid is reasonably stable, at the moment, but with more conventional plant dropping out, the power swings are going to get a bit more sever, and the DC type services will be getting worked more often. Classing it as a very infrequent event probably isn’t realistic, but what about infrequent events? I could see that it is possible that you could get to around the 4 events per month, although probably not at the full power swing. | This is a good point, and one that probably would benefit from a consistent consideration by DNOs. It might be sensible to base the frequency on the observed incidence of frequency excursions, over the last 18 months say, that trigger a specific level of response from such services. The response level might be set locally, and the P28 “frequency of event” set by the historic track of frequency excursions triggering that level of response. This can be calculated from the information NGESO publish monthly. This should be picked up as part of ongoing work to develop a common approach to BESSs between the DNOs. However, note that in the BESS discussions on 18/11 it was pointed out that the 3% limit essentially applies at any time once the transients have died away, so for BESS power swings the 3% probably applies in all cases, irrespective of frequency of event.

## Slide 33: Outstanding Issues – 3 – in progress
No | Issue | Assumed Status
114 | We have concerns relating the voltage step change for Battery Energy Storage Systems (BESS) when the systems are designated for fast frequency response. A number of network operators define step change to be full declared export to full declared import for real power P and for reactive power Q. The FFR contracts do not have a contracted obligation to reverse the direction of reactive power flow and no obligation to match the fast MW response with a MVAr response. When importing, there is no obligation to operate at a particular power factor only to operate within a +/-0.95 range. If a full MW ramp has occurred, it is reasonable to assume the system is under stress. To reverse Q at this point would be the worst of all strategies at it would exacerbate the stress of the system by introducing an unnecessary voltage step. It is likely that EFR or FFR BESS is located at a point with a high X/R ratio (close to a BSP or GSP). Therefore a unit change in Q would have at least 10x the impact on at the voltage step that of a unit change in P. This Q reversal condition appears to be based on a false assumption about the default behaviour of inverters under FFR. We believe it is a matter for the customer to demonstrate through simulation the voltage step change under power reversal. It is a matter for the customer to produce a reactive power strategy that meets the constraints of the D Code and the connection offer. Confirmation of the simulation can be done via commissioning tests with frequency injection for smaller steps. The imposition of this requirement distorts the market by essentially limiting the capacity of a BESS scheme to around half the capacity of other technologies thus creating hidden barrier to the penetration of the technology. The customer should demonstrate how they meet the voltage step change challenge through modelling and if necessary to verify through commissioning demonstration, not for the network operator to impose a control philosophy. | To be picked up in the BESS sessions

## Slide 34: Outstanding Issues – 4 – in progress
No | Issue | Draft response
117 | Need of Effective date: Even though the current amendment is classified as minor changes there are significant changes that would require time for manufacturers to update their PGMs to comply with recent requirements. Ex one of those is the Cyber security requirement. For changes like these that would require identifying and implement a solution to an already compliant machine would take significant time/cost. Hence any requirements that would require modification of existing hardware/software design would require an effective date from the current release (a minimum of 6 months is recommended) to enable the manufacturer to be compliant with up-to-date requirements. Currently, the exception is applicable only for certain technologies but is required to be made for all technologies. Please be mindful that it would take manufacturers some time to find an effective solution and to prove compliance. | We agree that any change of requirements will generally need a period before compliance is required to allow manufacturers and others to accommodate the new requirements. As you are probably aware the recent modification to introduce new requirements for storage built in a 12 month period for manufactures and developers to implement any required changes before compliance is required. It might be that this is what you have in mind when you refer to the exception in your last sentence? We do not believe that there are any changes that we have classified as minor in the most recent amendment that impose any new compliance requirements on manufacturers or developers. Even without a specific formal implementation period, manufacturers do have significant warning of even the minor changes. They are all discussed at the DER Technical Forum, often over more than one meeting, and are summarised in the slides for the Forum which are published. The changes are formally consulted on, providing both an opportunity to absorb the proposed changes, to assimilate the implications, and provide a response or challenge to the proposals. There is then a further period, usually a couple of months, before the modification is approved by the regulator and published. In regard of the new references for cybersecurity, there is no new specific performance or compliance requirements added at this time, simply an expectation that manufacturers will be applying industry good practices, as well as standards that manufacturers should already be working to, or adapting to. It might be that the requirements of the network licensees, as provider of critical national infrastructure, do become more specific in the future, but we recognize this is a developing area and we are initially seeking to apply guidance and a light touch. In conjunction with BEIS ENA has produced guidance for Distributed energy resources (DER) cyber security connection at https://www.energynetworks.org/operating-the-networks/managing-cyber-security. However we do note your concern over the most recent change and we will be happy to discuss any points relating to them, or modifications to ENA documents more generally.

## Slide 35: Outstanding Issues – 5 – in progress
No | Issue | Draft response
121 | Minor corrections in G99 It is proposed to replace all "electricity storage devices" with "Energy storage devices". Currently, all the devices store the electricity in alternative energy form not as electric/charge form directly. Clarification on which requirements apply for Energy storage devices. As the word is included in synchronous machine and power pack modules. Synchronous machine working is limited by the machine's ability to fulfill grid codes, but convertor-based devices can be altered to fulfill stringent requirements due to electronic capability. Hence for devices that employing different technologies, it is recommended to keep the requirements separately and not to mix them. Clarity on what is the acceptable minimum level of cyber security required at the power generating module. Is it required for the power gen and the power generating control system components to be at the same security level as the facility and the ENA network? | G99 is a network oriented documented and as such it is blind to the storage medium. From the network perspective storage consumes electricity when charging, and produces electricity when discharging – ie a flow of electricity in and out. Energy storage includes heat storage, and electric vehicles, where the final output is heat and mechanical energy respectively, not electricity. The wording of the synchronous power generating module has been chosen deliberately to cater for technologies such as compressed air storage where the same synchronous machine is used for compression and expansion. In all cases the power generating module has to meet all the requirements for that technology, irrespective of how it is constituted. There are no specific requirements in G99 or G98 in relation to cybersecurity; only a general obligation to manage cyber risks appropriately.

## Slide 36: Outstanding Issues – 5 continued.
No | Issue | Draft response
121 | Gas turbine can work independent of Heat recovery system and might start working before HR blocks starts. Hence recommended to show as two different modules instead of one. As once synchronized, it is possible for GT to run independently from the HR block. Modification of synchronous power generating module definition: recommend to remove energy storage device unless it is a flywheel like device that would be used as power generating device (ex. Mechanical UPS system - rotary UPS) but these devices are least used against grid as it supports power backup for short duration and just a load on grid until the grid fails. | Figure 4.1a shows a single power generating module comprising two separate power generating units. Whilst it is true that the gas turbine unit can be run independently, it is assumed that the steam turbine cannot. If the steam turbine were capable of independent operation then there would indeed be two separate synchronous PGMs. However as the steam turbine (a) cannot run independently and (b) normally runs in tandem with the gas turbine, the two units comprise a single SPGM. As per (a) above the definition caters for technologies such as hydro pumped storage and compressed air storage. Short term energy storage devices such as flywheels, DRUPs etc are specifically excluded from G99 – see section 7.1.2: “Equipment other than Generating Units (eg traction loads, lift motors etc) may act as a short term source of energy, and inject electrical energy into the Customer’s Installation when they operate in a regenerative mode. In general EREC G99 will not apply as there will be no need to make any specific design accommodation for such equipment as it is unlikely that they will support any possible power island for a significant length of time. Where such equipment can act as a source of electrical energy for more than a few seconds (say typically 20 s), the DNO will advise the Customer if the Customer’s Installation requires any special consideration such as reverse power protection on a case by case basis.”

## Slide 37: Outstanding Issues – 7
No | Issue | Assumed Status
122 | I represent a UK water industry working group responsible for the development and maintenance of electrical specifications. During recent work to update a specification for low voltage diesel generator sets, I was asked by the group to lobby the ENA technical committee responsible for G99 to consider relaxing the following clause in EREC G99: 7.3.3.1 parallel operation | 7.3.3.1 The Power Generating Module may be permitted to operate in parallel with the Distribution Network for no more than 5 minutes in any month, and no more frequently than once per week. If the duration of parallel connection exceeds this period, or this frequency, then the Power Generating Module shall be considered as if it is, or can be, operated in long-term parallel operation mode. An alternative frequency and duration may be agreed between the DNO and the Generator taking account of particular site circumstances and Power Generating Module design. An electrical time interlock should be installed to ensure that the period of parallel operation does not exceed the agreed period. The timer should be a separate device from the changeover control system such that failure of the auto changeover system will not prevent the parallel being broken. Notice that the highlighted text already allows for an agreement between the DNO and Generator to agree an appropriate testing regime, subject to there being a valid reason to do so. An alternative would be to fit full LoM protection and address any relevant points from 7.3.3.4, in which case the PGM would be treated as LTP. To be reviewed as part of the next update to G99.

## Slide 38
© ENA 2020